## Activity & Persons Exposed
TASK SPECIFIC RISK ASSESSMENT
Unit Address: |  |  |  |  | Tel: |  | Unit No: |  | Assessment No. | GRA 11
[5 empty] | Fax: |  | Assessment Date :
Review Date :
Unit Manager: |  |  |  | Line Manager : |  |  | Assessment completed by :
(Print Name & Job Title) :
Signature :
Copies to : | Operator |  |  | Team-Leader |  | Client | File
A. | Activity and or environment(s) assessed
Sump Pump - Routine Maintenance Electrical isolation, disconnect pipework, remove pump from sump, clean pump & sump / pit, check electrical connections, check condition of cable / flex, level switches & probes, inspect earth connections, check & record - motor insulation, earth continuity, running current.
General Comments : |  |  | Prevevnt motor/pump rotating when removing guards and cooling fan covers. Consider disinfecting sump before entering . NOTE. Warning notices required advising of trip hazards, open sump etc. NOTE . Advise those affected of maintenance work/ loss of service.authorised person and Supervisor will initiate Correct PTW. Supervisor will give operative a specific Method Statement / Safe System of Work prior to start which needs to read , understood,agrees and signed on to
B. | Persons Exposed |  | ü | if present. If not applicable - leave blank
ü | Company Employees |  |  |  | ü | Client Employees / Visitors |  | ü | Contractors
| New / Expectant Mums1 |  |  |  | ü | New Starters |  |  | Delivery Personnel
| Elderly (over 65 years) |  |  |  |  | Young Workers2 |  |  | Children2
| People outside of the site |  |  |  | ü | Agency Staff |  |  | Special Needs
ü | Night Workers3 |  |  |  | ü | Lone Workers |  | ü | Other Trainee, Insurance Inspector
1. |  | Separate 'New & Expectant Mothers Risk Assessment' to be completed for each person.
2. |  | Separate 'Children & Young Persons Risk Assessment' to be completed for each person.
3. |  | Separate 'Medical Questionnaire' to be completed for each night worker. Under the 'Working Time Regs' each night worker is entitled
to a free health assessment on request. Initially, this involves completion of a revised copy of the Company's 'Medical Questionnaire'.

## Hazards & Risks
C. | Hazards & Risks :Insert the following into the boxes below: H = High Risk-Likely to occur and serious injuries probable, M = Medium Risk -
Could occur and injuries could possible be serious, L = Low Risk-Unlikely to occur and if it did only minor injury likely. Leave blank if not applicable
Working Practices |  |  | Physical Injury |  |  | Environment
1 |  | Lone Worker | 21 |  | Assault / Violence | 42 | L | Working Outside / Weather
2 | M | Restricted/ Difficult to Access | 22 |  | Portable Equipment Hazards | 43 | H | Confined Spaces
3 |  | Hot Oil | 23 |  | Hand Tools | 44 |  | Access to First - Aid
4 |  | Spillages / Wet Floors | 24 |  | Large Equipment Hazards | 45 |  | Work Overhead
5 |  | Non routine practices | 25 | M | Moving Machine Parts | 46 | L | Lighting
6 |  | Radiological Controlled Areas | 26 | M | Slips, Trips & Falls | 47 |  | Extremes of Temperature
7 |  | Ergonomics | 27 | M | Falls from Heights | 48 |  | Ventilation
8 | M | Isolate / Lock off | 28 |  | Falling / Flying Objects | 49 |  | Access & Egress
Physical Agents |  |  | 29 |  | Transportation Hazards | Training (please tick)
9 | M | Electricity | 30 |  | Sharps | 50 | ü | Task Training
10 |  | Fire | 31 |  | Mobile Plant | 51 | ü | Basic Health & Safety
11 |  | Hot / Cold Objects | 32 |  | Drowning / Asphyxiation | 52 |  | Display Screen Equipment
12 |  | Noise / Vibration | Hazardous Substances |  |  | 53 | ü | Cleaning / COSHH / Manual Handling
13 |  | Animals | 33 | M | Contact with Chemicals | 54 | ü | Work Instructions
14 |  | Arc Flash / UV Light | 34 |  | Biological Hazards | 55 | ü | Permit To Work
15 |  | Explosion | 35 |  | Dust / Fumes / Gases / Vapours | 56 | ü | Method Statement / S.S.W.
16 |  | Pressure Systems / Gases | 36 | M | Vermin / Weils Disease | 57 | ü | Toolbox Talk Required
17 |  | Battery Rooms | 37 |  | Zoonotic (Animal to man) Diseases | Other Issues
Handling & Lifting |  |  | 38 |  | Hazardous Materials Control | 58 | ü | Documentation
18 | L | Handling of Loads | 39 | M | Foul Water | 59 | ü | Information / Signage
19 |  | Use of Lifting / Pulling Aids | 40 |  |  | 60 | ü | PPE / Equipment
20 |  | Mechanical Lifting Aids | 41 |  |  | 61 | ü | Site Survey

## Control Measures
(d) Significant Risks Identified |  |  | (e) | (f)
(High, Medium or Low Risk) |  |  | Control Measures to be Applied | Responsibilities
No | R | Working Practices |  | By Who | When
2 | M | Restricted/ Difficult to Access
4 |  | Spillages / Wet Floor | Water spillages need to be contained and cleared immediately. Wet floor signs need to be displayed whilst the spillage is being cleared and whilst the floor is being wet cleaned
8 | M | Isolate / Lock Off | Isolate and lock off system and purge | Authorised | Prior to
|  |  | with Electrical,mechanical and Secondary Isolation (Spade Off) | Person and | Start
Supervisor
Physical Agents
9 | M | Electricity | Consider increased risk of electric shock where water is present. Isolation and Normal precautions need to be taken to avoid contact with "live parts". Water not be used near live electrical equipment. Always check electric leads and plugs for loose wiring and damaged leads. | operative | Each time
10 |  | Fire | In case of fire, employees must know fire evacuation routes and local Fire Muster Point, Correct fire Extinguisher and Watch Person | operative | Each time
Handling & Lifting
18 |  | Handling of Loads | Manual Hadling Separate Assessment Required for each Location | operative | Each time
(d) Significant Risks Identified |  |  | (e) | (f)
(High, Medium or Low Risk) |  |  | Control Measures to be Applied | Responsibilities
No | R | Physical Injury |  | By Who | When
22 |  | Portable Equipment Hazards | All electrical equipment must be PAT tested and be within its date for re-testing. Users must do a quick visual check of the condition of the flex/plug etc prior to use. Before changing disposable parts on equipment (eg dust bags), the equipment must be disconnected from the electrical supply. Battery equipment must have the battery power disconnected/isolated. | operative | Each time
23 |  | Hand Tools | All Hand Tools are Checked priot ot use and the operative is competent in there Use. | operative | Each time
25 | M | Moving Machine Parts | Isolation of Equipment-Prevent motor/pump rotating when removing guards and cooling fan covers. | Supervisor | Each time
26 | M | Slips, Trips, Falls | Erect 'Caution' sign before commencing work to warn others of the hazard. Ensure all spillages are cleared up immediately. Ensure cabling is not caught/knotted as well as ensuring that it is not obstructing walkways | operative | Each time
27 |  | Falls from Heights | No work to be undertaken outside of guard-rails | operative | Each time
28 |  | Falling Objects | Secure all work equipment in such a manner that other workers will not be in danger of getting struck by falling objects | operative | Each time
30 |  | Sharps | Be aware of protruding objects | operative | Each time
32 |  | Drowning / Asphyxiation | Isolate sump from system to prevent ingress of water. Confined space assessment may apply | operative | Each time
(d) Significant Risks Identified |  |  | (e) | (f)
(High, Medium or Low Risk) |  |  | Control Measures to be Applied | Responsibilities
No | R | Hazardous Substances |  | By Who | When
33 | M | Contact with Chemicals | Assess chemicals used to disinfect / clean sump. All employees using chemicals must have been trained on their use, the dangers and the precautions to observe. Such training needs to include the use of Personal Protective Equipment. | General Manager | Before new chemicals are used
35 |  | Dust/ Fumes/ Gases/ Vapours | Correct PPE / RPE to be used | operative | Each time
36 | M | Vermin/ Weils Disease | 1. Carry out an assessment to determine sewage / rodent infection risk e.g. Weils Disease. 2. Assess chemicals used to disinfect / clean sump.
39 | M | Foul Water | Consider disinfecting the Sump before entering | operative | Each time
Environment
43 |  | Confined Spaces | Confined space working - A specific to location assessment is required to determine the level of risk & control measures to be implemented, see Shell CIP Site Procedures for further guidance. | Supervisor | Each time
44 |  | Access to First-Aid | For Minor illness/Injury Contact Occupational Health Centre or Security | All | Each time
For Major illness/ Injury Contact 5555
46 | L | Lighting | Reasonable Lighting (low voltage for Confined Space Work) | Supervisor | Each time
49 | M | Access and Egress | 1. Safe access required especially when manual handling. 2. Access arrangements must allow for emergency evacuation.
(d) Significant Risks Identified |  |  | (e) | (f)
(High, Medium or Low Risk) |  |  | Control Measures to be Applied | Responsibilities
No | R | Training (Tick) |  | By Who | When
50 | ü | Task Training | Where Confined Space Working is significant - Train Operatives in Procedures, Use of Personal Protective Equipment & Permit To Work System. | General Manager | Prior to start up
51 | ü | Basic Health & Safety | All employees should be trained to Level One Basic Health & Safety course | General Manager | Within 3 Months
53 | ü | Cleaning/COSHH/Manual H. | NOTE 1. Hazardous substances - 1. Carry out an assessment to determine sewage / rodent infection risk e.g. Weils Disease. 2. Assess chemicals used to disinfect / clean sump. All employees using chemicals must have been trained in their use, the dangers and the precautions to observe. Such training needs to include the use of Personal Protective Equipment. All cleaning staff must be trained in the dangers of slips, trips & falls and the precautions to observe. All staff to receive Manual Handling Training | General Manager | Prior to start up
54 | ü | Work Instruction | Service Works Help Desk | Supervisor | Each time
55 | ü | Permit to Work | authorised person and Supervisor will initiate Correct PTW | Supervisor | Each time
56 | ü | Method Statement / SSW | Supervisor will give operative a specific Method Statement / Safe System of Work prior to start which needs to read , understood,agrees and signed on to | Supervisor & Operative | Each time
57 | ü | Tool Box Talk Required | task specific tool box talk during programme of Works. | Supervisor | Each time
(d) Significant Risks Identified |  |  | (e) | (f)
(High, Medium or Low Risk) |  |  | Control Measures to be Applied | Responsibilities
No | R | Other Issues (Tick) |  | By Who | When
58 | ü | Documentation | HSE Guidelines for Employees and Contractors Site ProceduresComp Uk&I - Pressure System Safety Rules and Electrical Safety Rules Permit To Work for Confined Spaces, HSE (G) IND 258 Safe Working in Confined Space | operative | Each time
59 | ü | Information / Signage | Signs & Notices, Warn Passers - By of Open Sump, Site Information, Employee competent to Undertake The Work Erect 'Caution' signs and Barriers around the work area | operative | Each time
60 | ü | PPE / Equipment | Ensure appropriate PPE is worn. Tools, Meters & Instruments,Gas Monitoring Equipment, Lifting Equipment, Confined space equipment | operative | Each time
61 | ü | Site Survey | Visit Pump with Authorised Person prior to Permit Issue for correct Isolation and evaluate Risk and Equipment required

## Safe System of Work
Task: Sump Pump - Routine Maintenance
Significant Risks: (Detail all High & Medium Risks Here If This SSW is Not Attached to The Risk Assessment)
Is a ‘ Permit To Work’ required? | NO |  | YES | Ref. Number:
Is a designated work instruction required | NO |  | YES | Ref. Number:
Additional Training Required To Undertake this task (if any):
Additional Advice Regarding This Task Available From:
P.P.E. Requirements: Safety Helmet Eye Protection Face Masks Safety Footwear Respirators
High Visibility Clothing Gauntlets Gloves Hearing Defenders Special Gloves All Weather clothing
Proban Overalls
Other /PPE Required:
Additional Equipment Required:
Who Is Responsible for Management of This Task:
PROCEDURE:
‘SSW’ Prepared By:(Print) |  | Sign: |  |  | Date ‘SSW’ Last Reviewed: